## Predesign sheet
Pre-design sheet for an exergy optimised building design IEA ECBCS Annex 37 Steady state calculations for heating case Version 2.3
Object: |  | The ZUB Office Building, IEA Annex 37 Demoproject
1 | 1. Project data, boundary conditions
2 | Volume (inside) [m³] | V = | 6882.35
3 | Net floor area [m²] | AN = | 2202.35
4 | Indoor air temperature [°C] | qi = | 21
5 | Exterior air temperature [°C] | qe = | 0 | = qref Reference temperature
6 | 2. Heat losses
7 | 2.1 Transmission losses FT[W]
8 | Building part | Symbols | Area Ai | Thermal transmittance Ui | Ui * Ai | Temperature-correction-factor Fxi | Ui * Ai * Fxi
|  |  | [m²] | [W/(m²K)] | [W/K] | [ - ] | [W/K]
9 | Exterior wall | EW 1 | 430.36 | 0.13 | 55.9468 | 1 | 55.9468
10 |  | EW 2 | 4.02 | 0.85 | 3.417 | 1 | 3.417
11 |  | EW 3 | 277.71 | 0.27 | 74.9817 | 0.5 | 37.4909
12 |  | EW 4 | 5.55 | 0.17 | 0.9435 | 1 | 0.9435
13 | Window | W 1 | 482.35 | 0.8 | 385.88 | 1 | 385.88
14 |  | W 2 | 64.1 | 0.8 | 51.28 | 1 | 51.28
15 |  | W 3 | 104.62 | 0.9 | 94.158 | 1 | 94.158
16 |  | W 4 | 12.78 | 1.2 | 15.336 | 1 | 15.336
17 | Door | D 1 | 8.09 | 0.8 | 6.472 | 1 | 6.472
18 | Roof | R 1 | 368.56 | 0.16 | 58.9696 | 1 | 58.9696
19 |  | R 2 | 81.83 | 0.17 | 13.9111 | 1 | 13.9111
20 |  | R 3 |  |  | 0 | 1 | 0
21 | Upper story floor | R 4 |  |  | 0 | 0.8 | 0
22 |  | R 5 |  |  | 0 | 0.8 | 0
23 | Wall to roof rooms | RW 1 |  |  | 0 | 0.8 | 0
24 |  | RW 2 |  |  | 0 | 0.8 | 0
25 | Walls and floors to unheated rooms | uhW 1 |  |  | 0 | 0.5 | 0
26 |  | uhW 2 |  |  | 0 | 0.5 | 0
27 | Floors to ground. Areas of unheated cellar to ground | G 1 | 396.07 | 0.26 | 102.9782 | 0.6 | 61.7869
28 |  | G 2 | 86.09 | 0.2 | 17.218 | 0.6 | 10.3308
29 |  | G 3 | 12.06 | 0.2 | 2.412 | 0.6 | 1.4472
30 |  | G 4 |  |  | 0 | 0.6 | 0
31 |  | G 5 |  |  | 0 | 0.6 | 0
32 | S Ai = A = |  | 2334.19 | Specific transmission heat loss S Ui * Ai * Fxi = |  |  | 797.3698
33 | Transmission heat losses [W] | FT = S (Ui * Ai * Fxi) * (qi - qe)
|  | FT = | 797.3698 | 21 |  | FT = | 16744.7652
34 | 2.2 Ventilation heat losses FV [W]
35 | Air exchange rate [ach/h] | nd = | 0.6
36 | Heat exchanger efficiency [-] | hV = | 0.8
37 | Ventilation heat losses [W] | FV = (cp * r * V * nd * (1-hV)) * (qi - qe)
|  | FV = | 276.6705 | 21 |  | FV = | 5810.0799
38 | 3. Heat gains
39 | 3.1 Solar heat gains Fs [W]
40 | Window frame fraction [-] | Ff = | 0.3
41 | Orientation |  | Solar radiation Is,j |  | Window area AW,j | Total trans-mittance gj | Is,j * (1-Ff) * 0.9 * 0.9 *AW,j * gj 1)
|  |  | [W/m²] |  | [m²] | [ - ] | [W]
42 | south-east to south-west |  | 20 |  | 435.03 | 0.42 | 2071.9609
43 |  |  |  |  | 12.78 | 0.58 | 84.0566
44 | north-west to north-east |  | 20 |  | 31.26 | 0.42 | 148.8851
45 | [6 empty] | 0
46 | other directions |  | 50 |  | 81.9 | 0.42 | 975.1833
47 | [6 empty] | 0
48 | Dormer window with slope < 30° |  | 5 |  |  |  | 0
49 | Solar heat gains: | Fs = S (Is,j * (1-Ff) * AW,j * gj) |  |  |  | Fs = | 3280.0859
50 | 3.2 Internal Heat Gains Fi [W]
51 | Number of occupants [-]: | noo = | 12.5
52 | Internal gains of occupants [W]: | Fi,o = | noo * F"i,o
|  | Fi,o = | 12.5 | 80 |  | Fi,o = | 1000
53 | Spec. internal gains of equipment [W/m²]: | F"i,e = | 1.3622
54 | Internal gains of equipment [W]: | Fi,e = | F"i,e * AN
|  | Fi,e = | 1.3622 | 2202.35 |  | Fi,e = | 3000
55 | 4. Other uses
56 | Spec. lighting power [W/m²]: | pl = | 2
57 | Lighting power [W]: | Pl = pl * AN = Fi,l
|  | Pl = | 2 | 2202.35 |  | Pl = | 4404.7
58 | Spec. ventilation power [Wh/m³]: | pv = | 0.54
59 | Ventilation power [W]: | Pv = pv * V * nd
|  | Pv = | 0.54 | 6882.35 | 0.6 | Pv = | 2229.8814
60 | 5. Heat demand Fh [W]
61 | Heat demand [W]: | Fh = (FT + FV) - (Fs + Fi,o + Fi,e + Fi,l)
|  | Fh = | 22554.845 | 11684.7859 |  | Fh = | 10870.0591
62 | Specific heat demand [W/m²] | F''h = | Fh / AN
|  | F''h = | 10870.0591 | 2202.35 |  | F''h = | 4.9357
63 | 6. Heat production and emission
64 | Generation / Conversion: |  |  |  |  | Efficiency hG [-] | 0.89
[6 empty] | Primary energy factor source FP [-] | 2
[6 empty] | Quality factor of source Fq,S [-] | 0.21
[6 empty] | Max. supply temperature qS,max [°C] | 100
[6 empty] | Auxiliary energy paux,ge [W/kWheat] | 0.01
[6 empty] | Auxiliary energy paux,ge,const [W] | 0
[6 empty] | Part. environmental energy Frenew [-] | 0
65 | Storage: |  |  |  |  | Heat loss / efficiency hS [-] | 1
[6 empty] | Auxiliary energy paux,S [W/kWheat] | 0
[6 empty] | Solar fraction FS [-] | 0
66 | Distribution system: | Boiler position
Insulation
|  | Design temperature |  |  |  | Heat loss / efficiency hD [-] | 0.9604
|  | Temperature drop |  |  |  | Auxiliary energy paux,D [W/kWheat] | 164.1189
67 | Emission system: |  |  |  |  | Inlet temperature qin [°C] | 28
[6 empty] | Return temperature qret [°C] | 22
[6 empty] | Auxiliary energy paux,E [W/kWheat] | 0.2
[6 empty] | Max. heat emission pheat,max [W/m²] | 100
[6 empty] | Heat loss / efficiency hE [-] | 0.99
68 | DHW production system: |  |  |  |  | DHW demand VW [l/pers.d] | 0
[6 empty] | Efficiency hG,DHW [-] | 0
[6 empty] | Primary energy factor source FP,DHW [-] | 0
[6 empty] | Quality factor of source Fq,S,DHW [-] | 0
69 | 7. Results of exergy calculation
70 | Quality factor room air [-]: | Fq,room = 1 - Te / Ti | [5 empty] | Envelope
|  | Fq,room = | 0.071392 |  |  | Fq,room = | 0.071392
71 | Exergy load room [W]: | Exroom = Fh * Fq,room
|  | Exroom = | 10870.0591 | 0.071392 |  | Exroom = | 776.0369
72 | Heating temperature [°C]: | qheat = Dlogq /2 + qi | [5 empty] | Room air
|  | qheat = | 1.5417 | 21 |  | qheat = | 22.5417
73 | Quality factor air at heater [-]: | Fq,heater = 1 - Te / Theat
|  | Fq,heater = | 0.076234 |  |  | Fq,heater = | 0.076234
74 | Exergy load at heater [W]: | Exheat = Fh * Fq,heater
|  | Exheat = | 10870.0591 | 0.076234 |  | Exheat = | 828.6657
75 | Heat loss emission [W]: | Floss,E = Fh * (1/hE-1) | [5 empty] | Emission
|  | Floss,E = | 10870.0591 | 0.010101 |  | Floss,E = | 109.7986
76 | Auxiliary energy emission [W]: | Paux,E = paux,E * Fh
|  | Paux,E = | 0.0002 | 10870.0591 |  | Paux,E = | 2.174
77 | Exergy demand emission [W]: | DExemis = { (Fh+Floss,E) /(Tin - Tret)} * {(Tin - Tret) - Tref * ln (Tin / Tret )}
|  | DExemis = | 1829.9763 | 0.50292 |  | DExemis = | 920.3261
78 | Heat loss distributon [W]: | Floss,D = (Fh+Floss,E) * (1/hD-1) | [5 empty] | Distribution
|  | Floss,D = | 10979.8577 | 0.041233 |  | Floss,D = | 452.7305
79 | Auxiliary energy distribution [W]: | Paux,D = paux,D * (Fh+Floss,E)
|  | Paux,D = | 0.16412 | 10979.8577 |  | Paux,D = | 1802.0027
80 | Exergy demand distribution [W]: | DExdis = { Floss,D / DTdis } * {( DTdis - Tref * ln ( Tdis / Tdis - DTdis )}
|  | DExdis = | 90.5461 | 0.53155 |  | DExdis = | 48.1302
81 | Heat loss storage [W]: | Floss,S = (Fh+Floss,E+Floss,D) * (1/hS-1) | [5 empty] | Storage
|  | Floss,S = | 11432.5882 | 0 |  | Floss,S = | 0
82 | Auxiliary energy storage [W]: | Paux,S = paux,S * (Fh+Floss,E+Floss,D)
|  | Paux,S = | 0 | 11432.5882 |  | Paux,S = | 0
83 | Exergy demand storage [W]: | DExstor = { Floss,S / DTsto } * { DTsto - Tref * ln ( Tdis + DTdis / Tdis + DTdis - DTsto )}
|  | DExstor = |  | 0 |  | DExstor = | 0
84 | Req. energy of generation [W]: | Fge = (Fh+Floss,E+Floss,D+Floss,S) * (1-FS) / hB | [5 empty] | Generation
|  | Fge = | 11432.5882 | 1 | 0.89 | Fge = | 12845.6047
85 | Auxiliary energy generation [W]: | Paux,ge = paux,ge * (Fh+Floss,E+Floss,D+Floss,S) + paus,ge,const
|  | Paux,ge = | 1e-05 | 11432.5882 | 0 | Paux,ge = | 0.11433
86 | Exergy load generation [W]: | Exge = FGe * Fq,S
|  | Exge = | 12845.6047 | 0.21 |  | Exge = | 2697.577
87 | DHW energy demand [W] | PW = VW * cp * r * DT * noo / hG,DHW
|  | PW = | 0 | 0 | 0 | PW = | 0
88 | Exergy load plant [W]: | Explant = (Pl + PV) * Fq,electricity + PW * Fq,s,DHW
|  | Explant = | 6634.5814 | 0 |  | Explant = | 6634.5814
89 | Req. primary energy input [W]: | Eprim,tot = Fge * FP + (PI+PV+SPaux) * FP,electricity + PW * FP,DHW | [5 empty] | Energy transformation
|  | Eprim,tot = | 25691.2094 | 25316.6172 | 0 | Eprim,tot = | 51007.8266
90 | Add. renew. energy input [W]: | Erenew = Fge * Frenew + Eenvironment
|  | Erenew = |  |  |  | Erenew =
91 | Total exergy input [W]: | Extot = Fge*FP*Fq,S+(PI+PV+SPaux)*FP,elec*Fq,elec+PW*FP,DHW*Fq,S,DHW+Erenew*Fq,renew
|  | Extot = | 30711.7712 | 0 | 0 | Extot = | 30711.7712
1) 0.9 for shading and 0.9 for not orthogonal radiation
| Results in key figures |  |  |  | total | per Area | per Volume
| Energy input (primary and renewable energy + internal and solar gains) |  |  |  | 62692.6125 | 28.4662 | 9.1092
| Energy quality of envelope (heat demand + internal and solar gains) |  |  |  | 22554.845 | 10.2413 | 3.2772
| Total exergy system efficiency (exergy demand room / total exergy input) |  |  |  | 0.025268
| Exergy flexibility factor (exergy demand emission / total exergy input) |  |  |  | 0.057019
Error messages
Results of the calculation:
Figure 1: Exergy and energy flows through components
Figure 2: Exergy losses / consumption by components
Figure 3: Energy gains and losses
Figure 4: Exergy supply and demand
Authors:
| Dietrich Schmidt | Masanori Shukuya |  |  | Abdelaziz Hammache |  | Johann Zirngbl & Claude Francois
| KTH Building Technology | Musashi Institute of Technology |  |  | Natural Resources Canada |  | CSTB - Energy Systems and Environment
| Brinellvägen 34 | 1-28-1 Tamazutsumi Setagaya-ku |  |  | 1615 Lionel-Boulet |  | 84 avenue Jean Jaurès
| S-10044 Stockholm | Tokyo 158-8557 |  |  | Varennes Quebec J3X 1S6 |  | F-77421 Marne-la-Vallée Cedex 2
| SWEDEN | JAPAN |  |  | CANADA |  | FRANCE
With kind support of
Kirsten Höttges; Dep. of Building Physics; University of Kassel; D-34109 Kassel; GERMANY

## General Values
General Properties: |  | 20°C/1 bar |  |  | emitted heat per occupant [W]
cp Air room | 1.005 | kJ/kgK | 1.007 |  | 80
rho Air room | 1.2 | kg/m³ | 1.188
This is a COP heatpump calculation
T(low): | 22 | T(high): | 28
COP= | 5.5825
results |  |  | heat energy | electrical energy | system energy total | renewable | incl. free /rene. ener. | incl. internal & sloar gains | system exergy total | exergy incl. gains | rel exergy loss | rel energy loss
| input | 1 | 25691.2094 | 25316.6172 | 51007.8266 | 0 | 51007.8266 | 51007.8266 | 30711.7712 | 30711.7712 | 21379.6128 | 29723.3495 | Primary energy transform
| after prim trans | 2 | 12845.6047 | 8438.8724 | 21284.4771 | 0 | 21284.4771 | 21284.4771 | 9332.1584 | 9332.1584 | 5730.8598 | 8047.7122 | Generation
| after boiler | 3 | 11432.5882 | 1804.1767 | 13236.7649 | 0 | 13236.7649 | 13236.7649 | 3601.2986 | 3601.2986 | 0 | 0 | Storage
| after storage | 4 | 11432.5882 | 1804.1767 | 13236.7649 | 0 | 13236.7649 | 13236.7649 | 3601.2986 | 3601.2986 | 1850.1328 | 2254.7332 | Distribution
| after distributon | 5 | 10979.8577 | 2.174 | 10982.0317 | 0 | 10982.0317 | 10982.0317 | 1751.1658 | 1751.1658 | 922.5001 | 111.9726 | Emission
| after emission | 6 | 10870.0591 | 0 | 10870.0591 | 0 | 10870.0591 | 10870.0591 | 828.6657 | 828.6657 | 52.6288 | 0 | Room air
| after room | 7 | 10870.0591 | 0 | 10870.0591 | 0 | 10870.0591 | 22554.845 | 776.0369 | 1610.2388 | 776.0369 | 0 | Envelope
| after envelope | 8 | 10870.0591 | 0 | 10870.0591 | 0 | 10870.0591 | 22554.845 | 0 | 0
|  |  | heat | elec | tot
primary energy factor of electricity: | 3
results |  | energy gains | energy loss |  | results |  | exergy supply |  | exergy demand
| solar (windows) | 3280.0859 |  |  |  | solar (windows) | 2952.0773
| internal | 8404.7 |  |  |  | internal | 119.2971
| renewable |  |  |  |  | renewable | 0
| primary energy | 51007.8266 |  |  |  | primary exergy | 30711.7712
| transmision window |  | 11479.734 |  |  | Envelope |  |  | 776.0369
| transmission roof |  | 1530.4947 |  |  | Room Air |  |  | 52.6288
| transmission ground |  | 1544.8633 |  |  | Emission |  |  | 922.5001
| transmission walls |  | 2189.6732 |  |  | Distribution |  |  | 1850.1328
| ventilation |  | 5810.0799 |  |  | Storage |  |  | 0
| system heat losses |  | 562.5291 |  |  | Generation |  |  | 5730.8598
| inefficeint generation |  | 1413.0165 |  |  | Primary exergy |  |  | 21379.6128
| Electrical energy |  | 1804.291
| lighting |  | 4404.7
| ventilation elec |  | 2229.8814
| DHW |  | 0
| prim transform |  | 29723.3495
sum: |  | 62692.6125 | 62692.6125 |  |  | sum: | 33783.1456 |  | 30711.7712

## Values Generation-Conversion
System | Efficiency | Primary Energy Factor | Quality Factor of Source | Max. supply Temperature | Auxiliary Energy | Auxiliary Energy | part Environmental energy | Goal!!!
| [%] at 30% | [-] | [-] | [°C] | [W/kWheat] | [W] const | 11 | 11
0
Heat pump exhaust air/water | 2.9333 | 3 | 1 | 80 | 2 |  | 1.9333
Condensing boiler | 0.95 | 1.3 | 0.95 | 70 | 1.8 | 20 | 0 | Paux?
Co-generation | 0.85 | 1.37 | 0.95 | 100 | 0.02 |  | 0
Electric boiler | 0.98 | 3 | 1 | 100 | 0.02 |  | 0
Heat pump borehole water/glycol | 3.28 | 3 | 1 | 80 | 2 |  | 2.28
Heat pump external air/air | 3.5267 | 3 | 1 | 80 | 10 |  | 2.5267 | ok
Solar collector, flat plate | 0.7 | 0 | 0.23 | 80 | 0.01 |  | 1
Solar collector, vacuum tube | 0.5 | 0 | 0.35 | 150 | 0.01 |  | 1
Bio-mass/Wood | 0.65 | 0.1 | 0.95 | 70 | 1.8 | 20 | 0.9
District heat | 0.89 | 2 | 0.21 | 100 | 0.01 |  | 0
District heat Waste heat | 0.89 | 1 | 0.21 | 100 | 0.01 |  | 0
Standard boiler | 0.8 | 1.3 | 0.95 | 90 | 1.8 | 20 | 0 | Paux?
Ground heat pump water/water | 4.6133 | 3 | 1 | 35 | 2 |  | 3.6133
Air heat pump | 2.5 | 3 | 1 | 80 | 10 |  | 1.5 | ok
Heat pumps waterborne | 28 | Inlet Temperature emission:
External air/water | 3.5267
Exhaust air/water | 2.9333
Water / water | 4.6133
Water with glycol / water | 3.28

## Values Storage
System | Heat loss/Efficiency | Auxiliary Energy | Solar fraction |  | Goal!!!
| [-] | [W/kWheat] | [-] | 3 | 2
No storage | 1 | 0 | 0
Small / day storage | 0.95 | 2 | 0
Seasonal storage | 0.98 | 13.4 | 0.4 | 1
Assumed storagevolume for Small storage is 100I, for seasonal 10.000m3?
temp drop storage: | 0 | K

## Values Distribution
Emplacement | femplacement | Goal f1!!! |  | Source of all values: Johann Zirngibl and Claude Francois; CSTB, FRANCE
| [-] | 2
Inside envelope | 1
Outside envelope | 0.9
no distribution | 1 | 1
Insulation | finsulation | Goal f2!!!
| [-] | 4
No insulation | 0.7
Bad insulation | 0.9
Good insulation | 1
no distribution | 1 | 1
Design temperature | fdesigntemperature | Temperature | Goal f3!!!
| [-] | 1 | 2
Low (<35°C) | 1 | 35
Middle (<50°C) | 0.95 | 50
High (other) | 0.9 | 80
no distribution | 1 |  | 1 | 35
Temperature drop | ftemperaturedrop | temperature drop | Goal f4!!!
| [-] | [K] | 2
Low (<5K) | 0.98 | 5
Middle (<10K) | 0.99 | 10
High (other) | 1 | 20
no distribution | 1 |  | 0.98 | 5
Heat loss/Efficiency | Auxiliary Energy
[%] | [W/kWheat]
0.9604 | 164.1189 | Pr_Dif | 71576.375 | Pa
|  | MFL_AV | 0.00061909 | m3/s

## Values Emission
System | Supply Temperature | Return Temperature | Requiered auxiliary energy | Maximum heat emision | Heat loss/Efficiency |  | Goal!!!
| [°C] | [°C] | [W/kWheat] | [W/m²] | [%] |  | 7
Floor heating | 35 | 30 | 0 | 80 | 0.99
Wall heating | 50 | 40 | 0 | 150 | 0.95
Radiator | 70 | 60 | 0.2 | 100 | 0.95
Air heating/cooling | 35 | 25 | 0.81043 | 34 | 0.95
Ceiling heating | 50 | 40 | 0 | 130 | 0.95
Slab heating/cooling | 28 | 22 | 0.2 | 100 | 0.99
Free cooling-ventilation
HT radiators (DIN 255: 90/70) | 90 | 70 | 0 | 1000 | 0.95
HT radiators (DIN 255: 70/55) | 70 | 55 | 0 | 1000 | 0.95
HT radiators (DIN 255: 55/45) | 55 | 45 | 0 | 1000 | 0.95
HT radiators (DIN 255: 35/28) | 35 | 28 | 0 | 1000 | 0.95
LT radiators | 35 | 28 | 0 | 1000 | 0.95
Wall heating | 28 | 22 | 0.2 | 100 | 0.99
Radiating panel | 90 | 70 | 0 | 1000 | 0.95 | ?
Slab heating | 28 | 22 | 2 | 40 | 0.99
Direct electric heating |  |  |  | 1000 | 0.95

## Values DHW
System | Input Temperature | Supply Temperature | Flow | Efficiency boiler | Primary Energy Factor | Quality Factor of Source | Goal!!!
| [°C] | [°C] | [l/pers*d] | [%] | [-] | [-] | 2
No DHW production
Office; local electric boiler | 6 | 55 | 3 | 0.99 | 3 | 1
Dwelling; local electric boiler | 6 | 55 | 45 | 0.99 | 3 | 1
Dwelling; same boiler as for heating system | 6 | 55 | 45 | 0.84 | 2 | 0.21